## Sutron
Sutron Xlink500 Datalogger Settings
| GP1 | GP2 | GP3 | GP4 | GP5 | GP6 |  |  |  | Measurements
Site Name | sampling_on | sample_pacing | bottle_num | bottle_size_L | aliquot_vol_mL | pipe_diam | M1-Units | M3-MetaIndex | M3-Units | M12 - Alarm1 | Threshold | tx mode | M13-Units
Outfalls | [7 empty] | flow data source for pacing
Lomica | 0 | 40000 | 1 | 19 | 250 | 36 | gal | 13 (PT) | gal | High | 1" above current | Tx In
Ocean's 11 | 0 | 3000 | 1 | 19 | 250 | 24 | gal | 13 (PT) | gal | High | 0.5" or 0.5" above current | Tx In
Tazon | 0 | 10000 | 1 | 19 | 250 | 30 | gal | 8 (950) | gal | High | 0.5" or 0.5" above current | Tx In
Via Rancho | 0 | 3500 | 1 | 19 | 250 | 60 | cf | 13 (PT) | cf | High | 1" above current | Tx In
El Ku | 0 | 10000 | 1 | 19 | 250 |  | gal | 13 (PT) | gal | High | 0.5" | Tx In
Creeks
Del Dios | 0 | 1000 | 1 | 19 | 250 |  | cf | 13 | cf | High | 1" above current | Tx In | cfs
Felicita | 0 | 20000 | 1 | 19 | 250 |  | cf | 13 | cf | High | 1" above current | Tx In | cfs
Kit Carson | 0 | 30000 | 1 | 19 | 250 |  | cf | 13 | cf | High | 1" above current | Tx In | cfs
Cloverdale | 0 | 2000 | 1 | 19 | 250 |  | cf | 13 | cf | High | 1" above current | Tx In | cfs
Guejito | 0 | 1000 | 1 | 19 | 250 |  | cf | 13 | cf | High | 1" above current | Tx In | cfs
San Dieguito Creek | 0 | 1000 | 1 | 19 | 250 |  | cf | 13 | cf | High | 1" above current | Tx In | cfs
Sycamore | 0 | 1500 | 1 | 19 | 250 |  | cf | 13 | cf | High | 1" above current | Tx In | cfs
Green Valley | 0 | 40000 | 1 | 19 | 250 |  | cf | 13 | cf | High | 1" above current | Tx In | cfs
Moonsong | 0 | 30000 | 1 | 19 | 250 |  | cf | 13 | cf | High | 1" above current | Tx In | cfs

## Sigma 950 Flowmeter
Sigma 950 Flowmeter Settings |  |  |  |  | Primary Device | [11 empty] | Data Log | [7 empty] | If Velocity is being recorded
Site Name | Serial # (file ext) | Site ID | Location | Level Sensor | Primary Device | Shape | Diameter | Sampler Pacing | Flow units | Total flow units | Level units | Program Lock | RS-232 Baud rate | Modem Power | Days to Log | Rainfall Units | Rainfall | Flow Units | Flow | Level Units | Level | Velocity Units | Velocity | Memory Mode | Velocity Direction | Velocity Cutoff | Velocity Default
Outfalls
Lomica | ETZ | 914 | DW0914 - Lomica | Bubbler | Area Velocity | Circ Pipe | 36 | 40000 | gpm | gal | inches | Off | 19200 | Off | 33.8 |  | Not logged | gpm | 5min | in | 5min | fps | 5min | Wrap | Always Pos
Ocean's 11 | HXG | 11 | DW0011 - Oceans11 | Bubbler | Area Velocity | Circ Pipe | 24 | 3000 | gpm | gal | inches | Off | 19200 | Off | 204.4 |  | Not logged | gpm | 5min | in | 5min | fps | 5min | Wrap | Always Pos
Tazon | JEU | 317 | DW0317 - Tazon | Bubbler | Area Velocity | Circ Pipe | 30 | 10000 | gpm | gal | inches | Off | 19200 | Off | 204.4 |  | Not logged | gpm | 5min | in | 5min | fps | 5min | Wrap | Always Pos
Via Rancho | IFZ | 102 | HDG_102 Via Rancho Pkwy | Bubbler | Area Velocity | Circ Pipe | 60 | 3500 | cfs | cf | inches | Off | 19200 | Off | 204.4 |  | Not logged | cfs | 5min | in | 5min | fps | 5min | Wrap | Always Pos | 0.25 | 0.3
El Ku | DV2 | 101 | HDG_101_ElKu | Bubbler | Area Velocity | Trapezoidal | WidthBottom:12in, WidthTop:82in,ChanDepth:24in | 10000 | gpm | gal | inches | Off | 19200 | Off | 33.8 |  | Not logged | gpm | 5min | in | 5min | fps | 5min | Wrap | Always Pos | 0 | 0
Creeks | [5 empty] | Power:k1, n1, k2, n2
Del Dios | EUG | 1 | DelDios | Bubbler | Power Equation | 0.01,1.20,0.01,2.6 |  | 9999999999 cf | cfs | cf | inches | Off | 19200 | Off | 13.5 |  | Not logged | cfs | 1min | in | 1min | Not logged |  | Wrap | NA
Felicita | ETW | 3 | Felicita | Bubbler | Power Equation | 0.400,1.70,.01,2.5 |  | 999999999cf | cfs | cf | inches | Off | 19200 | Off | 13.5 |  | Not logged | cfs | 1min | in | 1min | Not logged |  | Wrap | NA
Kit Carson | IF1 | 3 | KitCarson | Bubbler | Power Equation | 0.200,2.00,0.015,1.80 |  | 999999999cf | cfs | cf | inches | Off | 19200 | Off | 81.8 | in | 1min | cfs | 1min | in | 1min | Not logged |  | Wrap | NA
Cloverdale | DUN |  | Cloverdale_draft | Bubbler | Power Equation | 1.00,1.25,0.00,3.90 |  | 999999999cf | cfs | cf | inches | Off | 19200 | Off | 13.5 |  | Not logged | cfs | 1min | in | 1min | Not logged |  | Wrap | NA | NA | NA
Guejito | JUK | 1 | Guejito | Bubbler | Power Equation | 0.01,1.00,0.03,2.55 |  | XXXXXXXXXX | cfs | cf | inches | Off | 19200 | Off | 81.8 |  | Not logged | cfs | 1min | in | 1min | Not logged |  | Wrap | NA | NA | NA
San Dieguito Creek | FNE | 1 | San Dieguito Creek | Bubbler | Power Equation | 0,3.0,0.015,3.0 |  | 999999999cf | cfs | cf | inches | Off | 19200 |  | 13.5 |  | Not logged | cfs | 1min | in | 1min | Not logged |  | Wrap | NA | NA | NA
Sycamore | EUC |  | Sycamore | Bubbler | Power Equation | 0,3.0,0,3.85 |  | 999999999cf | cfs | cf | inches | Off | 19200 | Off | 13.5 |  | Not logged | cfs | 1min | in | 1min | Not logged |  | Wrap | NA | NA | NA
Green Valley | DUH | 5 | GreenValley | Bubbler | Area Velocity | Circ Pipe | 36 | disabled | cfs | cf | inches | Off | 19200 | Off | 13.5 | in | 1min | Not logged |  | Not logged |  | Not logged |  | Wrap | NA
Moonsong | EUJ | 1 | Moonsong | Bubbler | Power Equation | 0.010, 1.2, 0.100, 2.50 |  | 999999999 cf | cfs | cf | inches | Off | 19200 | Off | 13.5 |  | Not logged | cfs | 1min | in | 1min | Not logged |  | Wrap | NA

## SD900 sampler
SD900 Sampler Settings | [15 empty] | Adv Sampling
Site Name | Bottle Quantity | Bottle Volume | Tubing Length | Tubing Size | Program Delay | Sample Collection | Take Sample Every | Override Time | Take first sample | Run Mode | Liquid Sensor | Sample Volume | Intake Rinses | Sample Retries | Site ID | Set Pt Sample | Special Output | Other stuff?
Outfalls
Lomica | 1 | 19L | 14 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250mL | 0 | 0 | DW0917 | Not checked (disabled) | Enabled-After Cycle | None checked
Ocean's 11 | 1 | 5Gal | 17 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250mL | 0 | 0 | DW0011 | Not checked (disabled) | Enabled-After Cycle | None checked
Tazon | 1 | 19L | 14 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250mL | 0 | 0 | 11359 | Not checked (disabled) | Enabled-After Cycle | None checked
Via Rancho | 1 | 20L | 11 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250mL | 0 | 0 | HDG102 | Not checked (disabled) | Enabled-After Cycle | None checked
El Ku | 1 | 19L | 6 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250mL | 0 | 0 | ElKu | Not checked (disabled) | Enabled-After Cycle | None checked
Creeks
Del Dios | 1 | 20L | 26 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250mL | 0 | 0 | DW053 | Not checked (disabled) | Not checked (disabled) | None checked
Felicita | 1 | 19L | 25 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250mL | 0 | 0 | 5 | Not checked (disabled) | Not checked (disabled) | None checked
Kit Carson | 1 | 19L | 16 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250mL | 0 | 0 | 0000 | Not checked (disabled) | Not checked (disabled) | None checked
Cloverdale | 1 | 19L | 82 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250 mL | 0 | 0 | Clover | Not checked (disabled) | Not checked (disabled) | None checked
Guejito | 1 | 19L | 19 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250 mL | 0 | 0 | Guejito | Not checked (disabled) | Not checked (disabled) | None checked
San Dieguito Creek | 1 | 19L | 65 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250 mL | 0 | 0 | SDC01 | Not checked (disabled) | Not checked (disabled) | None checked
Sycamore | 1 | 19L | 27 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250 mL | 0 | 0 | SYC2 | Not checked (disabled) | Not checked (disabled) | None checked
Green Valley | 1 | 19L | 51 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250mL | 0 | 0 | 5 | Not checked (disabled) | Not checked (disabled) | None checked
Moonsong | 1 | 19L | 26 ft | 3/8" Teflon | Disabled | Flow based | 1 counts | Disabled | After Interval | Continuous | Enabled | 250mL | 0 | 0 | PVC | Not checked (disabled) | Not checked (disabled) | None checked

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only