## Sheet1
To calculate the register address, use the last 5 digits of the register number (0066) and subtract 1. The register address for register number 40066 is 65 (0x41 hex).
To calculate the checksum: https://www.lammertbies.nl/comm/info/crc-calculation input address up to checksum bytes and select "Hex". Compute the CRC-16 Modbus, reverse 2 character chunks ex. 0x5A63 >> 635A
These values are hexadecimal bytes, not ASCII characters.
|  | RTU Message | [7 empty] | Response |  |  |  |  | Read Result Register | [5 empty] | Response
Description | Message | Address | Function | StartRegister | NumRegisters | ByteCount | Data | Checksum |  | Address | Function | StartRegister | NumRegisters | Checksum |  | Address | Function | StartRegister | NumRegisters | Checksum |  | Address | Function | Byte Count | Register data | Checksum
|  | 1 byte; 0-247 | 1 byte; |  |  |  | Var # of bytes | 2 bytes |  | 1 byte; 0-247 | 1 byte
Turn pump on(fwd): 0 | 021026CF00020400008000635A | 02 | 10 | 26CF | 0002 | 04 | 00008000 | 635A | 021026CF00027A8C | 02 | 10 | 26CF | 0002 | 7A8C | 020326CE0001EE8E | 02 | 03 | 26CE | 0001 | EE8E | 02030200013D84 | 02 | 03 | 02 | 0001 | 3D84
Turn pump off: 0 | 021026CF00020400008001A29A | 02 | 10 | 26CF | 0002 | 04 | 00008001 | A29A | 021026CF00027A8C | 02 | 10 | 26CF | 0002 | 7A8C | 020326CE0001EE8E | 02 | 03 | 26CE | 0001 | EE8E | 02030200013D84 | 02 | 03 | 02 | 0001 | 3D84
Change state - Ready: 0 | 021026CF000204000080046299 | 02 | 10 | 26CF | 0002 | 04 | 00008004 | 6299 | 021026CF00027A8C | 02 | 10 | 26CF | 0002 | 7A8C | 020326CE0001EE8E | 02 | 03 | 26CE | 0001 | EE8E
Change state - Complete: 1 | 021026CF000204000180043359 | 02 | 10 | 26CF | 0002 | 04 | 00018004 | 3359 | 021026CF00027A8C | 02 | 10 | 26CF | 0002 | 7A8C | 020326CE0001EE8E | 02 | 03 | 26CE | 0001 | EE8E
Change state - Halted: 2 | 021026CF00020400028004C359 | 02 | 10 | 26CF | 0002 | 04 | 00028004 | C359 | 021026CF00027A8C | 02 | 10 | 26CF | 0002 | 7A8C | 020326CE0001EE8E | 02 | 03 | 26CE | 0001 | EE8E
Change state - Restart: 3 | 021026CF000204000380049299 | 02 | 10 | 26CF | 0002 | 04 | 00038004 | 9299 | 021026CF00027A8C | 02 | 10 | 26CF | 0002 | 7A8C | 020326CE0001EE8E | 02 | 03 | 26CE | 0001 | EE8E
Change state - Resume: 4 | 021026CF000204000480042358 | 02 | 10 | 26CF | 0002 | 04 | 00048004 | 2358 | 021026CF00027A8C | 02 | 10 | 26CF | 0002 | 7A8C | 020326CE0001EE8E | 02 | 03 | 26CE | 0001 | EE8E | 02030200013D84 | 02 | 03 | 02 | 0001 | 3D84
Grab Sample | 021026CF000204006480076347 | 02 | 10 | 26CF | 0002 | 04 | 00648007 | 6347 | 021026CF00027A8C | 02 | 10 | 26CF | 0002 | 7A8C | 020326CE0001EE8E | 02 | 03 | 26CE | 0001 | EE8E | 02030200027D85 | 02 | 03 | 02 | 0002 | 7D85
| hex converter: https://www.rapidtables.com/convert/number/decimal-to-hex.html?x=32769 | [5 empty] | 64 is hex for 100 (mL for grab sample) | 2769
8007 is hex for 32775 the program sequence number
set_time | F7 10 26 FC 00 02 04 00 01 00 00 00 02 94 | F7 | 10 | 26 FC | 00 02 | 04 | 00 01 00 00 00 | 02 94
set_interval | F7 10 00 84 00 01 02 00 02 16 71 | F7 | 10 | 00 84 | 00 01 | 02 | 00 02 | 16 71

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only